## Model Instances
Bauer BSM-WS36A-H01-1311-0000 Modbus Model Instance Overview
Colors
Additional Data for User Documentation
Markers
Data Model Address | Address | ID | Payload | Label | Label User Documentation | Name | Aliases | Description User Documentation
40001 | 40000 |  | 0 | SunSpec ID | SunSpec-ID |  |  | Identifikationsnummer
40003 | 40002 | 1 | 66 | Common | Common-Block | common | common, cb | Standard SunSpec-Modell mit allgemeinen Informationen
40071 | 40070 | 10 | 4 | Serial Interface Header | Schnittstellen-Header | model_10 | serial_interface_header, sih | Standard SunSpec-Modell mit allgemeinen Informationen zu einer Kommunikationsschnittstelle
40077 | 40076 | 17 | 12 | Serial Interface | Serielle Schnittstelle | model_17 | serial_interface, si | Standard SunSpec-Modell einer seriellen Schnittstelle
40091 | 40090 | 203 | 105 | AC Meter | Dreiphasen-Energiezähler | ac_meter | ac_meter, tpm | Standard SunSpec-Modell eines Dreiphasen-Energiezählers
40198 | 40197 | 64900 | 300 | Signing Meter | Signierender Zähler | bsm | bs_meter, bsm, sm | Eigenes Modell mit erweiterten Informationen für diesen signierenden Energiezähler
40500 | 40499 | 64902 | 20 | Communication Module Firmware Hash | Hash Firmware Kommunikationsmodul | bsm_blob | cm_firmware_hash, cfwh | Eigenes Modell mit der binären Darstellung des Hashs der Firmware des Kommunikationsmoduls
40522 | 40521 | 64901 | 260 | Signed Current Snapshot | Signierter Momentanzustand | bsm_snapshot | signed_current_snapshot, scs | Eigenes Modell eines signierten Schnappschusses einer Auswahl der Daten des Momentanzustands des Gerätes
40776 | 40775 | 64901 | 260 | Signed Turn-On Snapshot | Signierte Schalt-Mess-Koordination Einschalten | bsm_snapshot | signed_turn_on_snapshot, stons | Eigenes Modell eines signierten Schnappschusses einer Auswahl von Daten, die im Rahmen des Einschaltens des Digitalausgangs über die Schalt-Mess-Koordination erhoben wurden
41030 | 41029 | 64901 | 260 | Signed Turn-Off Snapshot | Signierte Schalt-Mess-Koordination Ausschalten | bsm_snapshot | signed_turn_off_snapshot, stoffs | Eigenes Modell eines signierten Schnappschusses einer Auswahl von Daten, die im Rahmen des Ausschaltens des Digitalausgangs über die Schalt-Mess-Koordination erhoben wurden
41284 | 41283 | 64901 | 252 | Signed Start Snapshot | Signierter Messung Start | bsm_snapshot | signed_start_snapshot, sss | Eigenes Modell eines signierten Schnappschusses einer Auswahl von Daten, die zum Start eines Ladevorgangs (ohne Schalten) erhoben wurden
41538 | 41537 | 64901 | 252 | Signed End Snapshot | Signierte Messung Ende | bsm_snapshot | signed_end_snapshot, ses | Eigenes Modell eines signierten Schnappschusses einer Auswahl von Daten, die zum Beenden eines Ladevorgangs (ohne Schalten) erhoben wurden
41792 | 41791 | 64903 | 498 | OCMF Signed Current Snapshot | Signierter Momentanzustand OCMF | bsm_ocmf | ocmf_signed_current_snapshot, oscs | Eigenes Modell einer OCMF-Darstellung des signierten Momentanzustands
42292 | 42291 | 64903 | 498 | OCMF Signed Turn-On Snapshot | Signierte Schalt-Mess-Koordination Einschalten OCMF | bsm_ocmf | ocmf_signed_turn_on_snapshot, ostons | Eigenes Modell einer OCMF-Darstellung der signierten Schalt-Mess-Koordination Einschalten
42792 | 42791 | 64903 | 498 | OCMF Signed Turn-Off Snapshot | Signierte Schalt-Mess-Koordination Ausschalten OCMF | bsm_ocmf | ocmf_signed_turn_off_snapshot, ostoffs | Eigenes Modell einer OCMF-Darstellung der signierten Schalt-Mess-Koordination Ausschalten
43292 | 43291 | 64903 | 498 | OCMF Signed Start Snapshot | Signierte Messung Start | bsm_ocmf | ocmf_signed_start_snapshot, osss | Eigenes Modell einer OCMF-Darstellung der signierten Messung zum Start
43792 | 43791 | 64903 | 498 | OCMF Signed End Snapshot | Signierte Messung Ende | bsm_ocmf | ocmf_signed_end_snapshot, oses | Eigenes Modell einer OCMF-Darstellung der signierten Messung zum Ende
44292 | 44291 | 65535 | 0 | End | Ende |  |  | Standard SunSpec-Modell zur Anzeige des Endes der Modelle dieses Gerätes

## Registers
Bauer BSM-WS36A-H01-1311-0000 Modbus Register Overview
Colors
Data Points Fixed Block
Data Points Repeating Block
Reserved Data Points
Additional Data for User Documentation
Description of Bitfields, Enums, …
Model Instance: Common
Model: Common
Description: All SunSpec compliant devices must include this as the first model
Notes:
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40003 | 40002 | 0 | 1 | ID | Model ID | Modell-ID | 1 | 1 | uint16 |  |  | r | nein | true |  | SunSpec Common-Modell
header |  | 40004 | 40003 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 66 | 66 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40005 | 40004 | 2 | 16 | Mn | Manufacturer | Hersteller |  |  | string |  |  | r | nein | true | Well known value registered with SunSpec for compliance
fixed |  | 40021 | 40020 | 18 | 16 | Md | Model | Modellbezeichnung |  |  | string |  |  | r | nein | true | Manufacturer specific value (32 chars)
fixed |  | 40037 | 40036 | 34 | 8 | Opt | Options | Reserviert |  |  | string |  |  | r | nein | false | Manufacturer specific value (16 chars)
fixed |  | 40045 | 40044 | 42 | 8 | Vr | Version | Versionsnummer des Gerätes |  |  | string |  |  | r | nein | false | Manufacturer specific value (16 chars)
fixed |  | 40053 | 40052 | 50 | 16 | SN | Serial Number | Seriennummer |  |  | string |  |  | r | nein | true | Manufacturer specific value (32 chars)
fixed |  | 40069 | 40068 | 66 | 1 | DA | Device Address | Modbus-Adresse | 0 | 42 | uint16 |  |  | rw | ja | false | Modbus device address
fixed |  | 40070 | 40069 | 67 | 1 | Pad |  | Padding | 0 | 206696 | pad |  |  | r | nein | false | Force even alignment
Model Instance: Serial Interface Header
Model: Communication Interface Header
Description: To be included first for a complete interface description
Notes:
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40071 | 40070 | 0 | 1 | ID | Model ID | Modell-ID | 10 | 10 | uint16 |  |  | r | nein | true |  | SunSpec-Modell Schnittstellen-Header (Interface Header)
header |  | 40072 | 40071 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 4 | 4 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40073 | 40072 | 2 | 1 | St | Interface Status | Status | 0 | 1 | enum16 |  |  | r | nein | true | Overall interface status | Siehe Kapitel 16.4.
fixed |  | 40074 | 40073 | 3 | 1 | Ctl | Interface Control | Steuerung | 0 | 65535 | uint16 |  |  | rw | nein | false | Overall interface control (TBD) | Bedeutung dieses Wertes in der Spezifikation noch offen
fixed |  | 40075 | 40074 | 4 | 1 | Typ | Physical Access Type | Medium | 0 | 2 | enum16 |  |  | r | nein | false | Enumerated value. Type of physical media | Fest 2 für verdrilltes Adernpaar (Twisted Pair)
fixed |  | 40076 | 40075 | 5 | 1 | Pad |  | Padding | 0 | 32768 | pad |  |  | r | nein | false
enum16 | St |  |  |  |  | DOWN | down |  | 0 | [7 empty] | Interface is down
enum16 | St |  |  |  |  | UP | up |  | 1 | [7 empty] | Interface is up
enum16 | St |  |  |  |  | FAULT | fault |  | 2 | [7 empty] | Interface is in a fault state
enum16 | Typ |  |  |  |  | UNKNOWN | unknown |  | 0 | [7 empty] | Unkown media
enum16 | Typ |  |  |  |  | INTERNAL | internal |  | 1 | [7 empty] | Internal e.g. embbedded switch
enum16 | Typ |  |  |  |  | TWISTED_PAIR | twisted pair |  | 2 | [7 empty] | Twisted Pair
enum16 | Typ |  |  |  |  | FIBER | fiber |  | 3 | [7 empty] | Fiber
enum16 | Typ |  |  |  |  | WIRELESS |  |  | 4
enum16 | Typ | [5 empty] | wifi | [9 empty] | WIFI
Model Instance: Serial Interface
Model: Serial Interface
Description: Include this model for serial interface configuration support
Notes:
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40077 | 40076 | 0 | 1 | ID | Model ID | Modell-ID | 17 | 17 | uint16 |  |  | r | nein | true |  | SunSpec-Modell serielle Schnittstelle
header |  | 40078 | 40077 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 12 | 12 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40079 | 40078 | 2 | 4 | Nam | Name | Name |  |  | string |  |  | rw | nein | false | Interface name (8 chars) |  | Standard model declares this data point writeable but we don’t support this.
fixed |  | 40083 | 40082 | 6 | 2 | Rte | Rate | Baud-Rate | 0 |  | uint32 | bps |  | rw | ja | true | Interface baud rate in bits per second
fixed |  | 40085 | 40084 | 8 | 1 | Bits | Bits | Bits pro Zeichen | 0 | 8 | uint16 |  |  | rw | nein | true | Number of data bits per character | Fest 8 | Standard model declares this data point writeable but we don’t support this.
fixed |  | 40086 | 40085 | 9 | 1 | Pty | Parity | Parität | 0 | 2 | enum16 |  |  | rw | nein | true | Bitmask value. Parity setting | Fest 2 für gerade Parität | Standard model declares this data point writeable but we don’t support this.
fixed |  | 40087 | 40086 | 10 | 1 | Dup | Duplex | Duplex | 0 | 1 | enum16 |  |  | rw | nein | false | Enumerated value. Duplex mode | Fest 1 für Halbduplex | Standard model declares this data point writeable but we don’t support this.
fixed |  | 40088 | 40087 | 11 | 1 | Flw | Flow Control | Flusskontrolle | 0 | 0 | enum16 |  |  | rw | nein | false | Flow Control Method | Fest 0 für keine Flusskontrolle | Standard model declares this data point writeable but we don’t support this.
fixed |  | 40089 | 40088 | 12 | 1 | Typ | Interface Type | Schnittstellentyp | 0 | 2 | enum16 |  |  | r | nein | false | Enumerated value. Interface type | Fest 2 für RS-485
fixed |  | 40090 | 40089 | 13 | 1 | Pcol | Protocol | Protokoll | 0 | 1 | enum16 |  |  | r | nein | false | Enumerated value. Serial protocol selection | Fest 1 für Modbus
enum16 | Pty |  |  |  |  | NONE | none |  | 0 | [7 empty] | No Parity
enum16 | Pty |  |  |  |  | ODD | odd |  | 1 | [7 empty] | Odd Parity
enum16 | Pty |  |  |  |  | EVEN | even |  | 2 | [7 empty] | Even Parity
enum16 | Dup |  |  |  |  | FULL | full |  | 0 | [7 empty] | Full Duplex
enum16 | Dup |  |  |  |  | HALF | half |  | 1 | [7 empty] | Half Duplex
enum16 | Flw |  |  |  |  | NONE | none |  | 0 | [7 empty] | No flow control
enum16 | Flw |  |  |  |  | HW | hardware |  | 1 | [7 empty] | Hardware flow control
enum16 | Flw |  |  |  |  | XONXOFF | software |  | 2 | [7 empty] | Soft (XON/XOFF) flow control
enum16 | Typ |  |  |  |  | UNKNOWN | unknown |  | 0 | [7 empty] | Unknown interface type
enum16 | Typ |  |  |  |  | RS232 | RS232 |  | 1 | [7 empty] | RS232 interface type
enum16 | Typ |  |  |  |  | RS485 | RS485 |  | 2 | [7 empty] | RS485 interface type
enum16 | Pcol |  |  |  |  | UNKNOWN | unknown |  | 0 | [7 empty] | Unknown protocol
enum16 | Pcol |  |  |  |  | MODBUS | Modbus |  | 1 | [7 empty] | Modbus protocol
enum16 | Pcol |  |  |  |  | VENDOR | vendor specific |  | 2
Model Instance: AC Meter
Model: wye-connect three phase (abcn) meter
Description:
Notes:
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40091 | 40090 | 0 | 1 | ID | Model ID | Modell-ID | 203 | 203 | uint16 |  |  | r | nein | true |  | SunSpec-Modell Dreiphasen-Energiezähler (Three Phase Meter)
header |  | 40092 | 40091 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 105 | 105 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40093 | 40092 | 2 | 1 | A | Amps | Momentaner Strom Total | 0 |  | int16 | A | A_SF | r | nein | true | Total AC Current
fixed |  | 40094 | 40093 | 3 | 1 | AphA | Amps PhaseA | Momentaner Strom Phase L1 | 0 |  | int16 | A | A_SF | r | nein | true | Phase A Current
fixed |  | 40095 | 40094 | 4 | 1 | AphB | Amps PhaseB | Momentaner Strom Phase L2 | 0 |  | int16 | A | A_SF | r | nein | true | Phase B Current
fixed |  | 40096 | 40095 | 5 | 1 | AphC | Amps PhaseC | Momentaner Strom Phase L3 | 0 |  | int16 | A | A_SF | r | nein | true | Phase C Current
fixed |  | 40097 | 40096 | 6 | 1 | A_SF |  | Skalierungsfaktor Strom | 0 |  | sunssf |  |  | r | nein | true | Current scale factor
fixed |  | 40098 | 40097 | 7 | 1 | PhV | Voltage LN | Reserviert | 0 |  | int16 | V | V_SF | r | nein | true | Line to Neutral AC Voltage (average of active phases)
fixed |  | 40099 | 40098 | 8 | 1 | PhVphA | Phase Voltage AN | Momentane Spannung Phase L1 | 0 |  | int16 | V | V_SF | r | nein | true | Phase Voltage AN
fixed |  | 40100 | 40099 | 9 | 1 | PhVphB | Phase Voltage BN | Momentane Spannung Phase L2 | 0 |  | int16 | V | V_SF | r | nein | true | Phase Voltage BN
fixed |  | 40101 | 40100 | 10 | 1 | PhVphC | Phase Voltage CN | Momentane Spannung Phase L3 | 0 |  | int16 | V | V_SF | r | nein | true | Phase Voltage CN
fixed |  | 40102 | 40101 | 11 | 1 | PPV | Voltage LL | Reserviert | 0 |  | int16 | V | V_SF | r | nein | true | Line to Line AC Voltage (average of active phases)
fixed |  | 40103 | 40102 | 12 | 1 | PhVphAB |  | Reserviert | 0 |  | int16 | V | V_SF | r | nein | true
fixed |  | 40104 | 40103 | 13 | 1 | PhVphBC |  | Reserviert | 0 |  | int16 | V | V_SF | r | nein | true
fixed |  | 40105 | 40104 | 14 | 1 | PhVphCA |  | Reserviert | 0 |  | int16 | V | V_SF | r | nein | true
fixed |  | 40106 | 40105 | 15 | 1 | V_SF |  | Skalierungsfaktor Spannung | 0 |  | sunssf |  |  | r | nein | true | Voltage scale factor
fixed |  | 40107 | 40106 | 16 | 1 | Hz | Hz | Momentane Netzfrequenz | 0 |  | int16 | Hz | Hz_SF | r | nein | true | Frequency
fixed |  | 40108 | 40107 | 17 | 1 | Hz_SF |  | Skalierungsfaktor Netzfrequenz | 0 |  | sunssf |  |  | r | nein | false | Frequency scale factor
fixed |  | 40109 | 40108 | 18 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | true | Total Real Power
fixed |  | 40110 | 40109 | 19 | 1 | WphA | Watts phase A | Mom. Wirk-Leistung Phase L1 | 0 |  | int16 | W | W_SF | r | nein | false
fixed |  | 40111 | 40110 | 20 | 1 | WphB | Watts phase B | Mom. Wirk-Leistung Phase L2 | 0 |  | int16 | W | W_SF | r | nein | false
fixed |  | 40112 | 40111 | 21 | 1 | WphC | Watts phase C | Mom. Wirk-Leistung Phase L3 | 0 |  | int16 | W | W_SF | r | nein | false
fixed |  | 40113 | 40112 | 22 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | true | Real Power scale factor
fixed |  | 40114 | 40113 | 23 | 1 | VA | VA | Momentane Schein-Leistung Total | 0 |  | int16 | VA | VA_SF | r | nein | false | AC Apparent Power
fixed |  | 40115 | 40114 | 24 | 1 | VAphA | VA phase A | Mom. Schein-Leistung Phase L1 | 0 |  | int16 | VA | VA_SF | r | nein | false
fixed |  | 40116 | 40115 | 25 | 1 | VAphB | VA phase B | Mom. Schein-Leistung Phase L2 | 0 |  | int16 | VA | VA_SF | r | nein | false
fixed |  | 40117 | 40116 | 26 | 1 | VAphC | VA phase C | Mom. Schein-Leistung Phase L3 | 0 |  | int16 | VA | VA_SF | r | nein | false
fixed |  | 40118 | 40117 | 27 | 1 | VA_SF |  | Skalierungsfaktor Scheinleistung | 0 |  | sunssf |  |  | r | nein | false | Apparent Power scale factor
fixed |  | 40119 | 40118 | 28 | 1 | VAR | VAR | Momentane Blind-Leistung Total | 0 |  | int16 | var | VAR_SF | r | nein | false | Reactive Power
fixed |  | 40120 | 40119 | 29 | 1 | VARphA | VAR phase A | Mom. Blind-Leistung Phase L1 | 0 |  | int16 | var | VAR_SF | r | nein | false
fixed |  | 40121 | 40120 | 30 | 1 | VARphB | VAR phase B | Mom. Blind-Leistung Phase L2 | 0 |  | int16 | var | VAR_SF | r | nein | false
fixed |  | 40122 | 40121 | 31 | 1 | VARphC | VAR phase C | Mom. Blind-Leistung Phase L3 | 0 |  | int16 | var | VAR_SF | r | nein | false
fixed |  | 40123 | 40122 | 32 | 1 | VAR_SF |  | Skalierungsfaktor Blindleistung | 0 |  | sunssf |  |  | r | nein | false | Reactive Power scale factor
fixed |  | 40124 | 40123 | 33 | 1 | PF | PF | Reserviert | 0 |  | int16 | Pct | PF_SF | r | nein | false | Power Factor
fixed |  | 40125 | 40124 | 34 | 1 | PFphA | PF phase A | Momentaner Formfakter Phase L1 | 0 |  | int16 | Pct | PF_SF | r | nein | false
fixed |  | 40126 | 40125 | 35 | 1 | PFphB | PF phase B | Momentaner Formfakter Phase L2 | 0 |  | int16 | Pct | PF_SF | r | nein | false
fixed |  | 40127 | 40126 | 36 | 1 | PFphC | PF phase C | Momentaner Formfakter Phase L3 | 0 |  | int16 | Pct | PF_SF | r | nein | false
fixed |  | 40128 | 40127 | 37 | 1 | PF_SF |  | Skalierungsfaktor Formfaktor | 0 |  | sunssf |  |  | r | nein | false | Power Factor scale factor
fixed |  | 40129 | 40128 | 38 | 2 | TotWhExp | Total Watt-hours Exported | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | true | Total Real Energy Exported
fixed |  | 40131 | 40130 | 40 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40133 | 40132 | 42 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40135 | 40134 | 44 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40137 | 40136 | 46 | 2 | TotWhImp | Total Watt-hours Imported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | TotWh_SF | r | nein | true | Total Real Energy Imported
fixed |  | 40139 | 40138 | 48 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40141 | 40140 | 50 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40143 | 40142 | 52 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C | Reserviert | 0 |  | acc32 | Wh | TotWh_SF | r | nein | false
fixed |  | 40145 | 40144 | 54 | 1 | TotWh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | true | Real Energy scale factor
fixed |  | 40146 | 40145 | 55 | 2 | TotVAhExp | Total VA-hours Exported | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false | Total Apparent Energy Exported
fixed |  | 40148 | 40147 | 57 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40150 | 40149 | 59 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40152 | 40151 | 61 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40154 | 40153 | 63 | 2 | TotVAhImp | Total VA-hours Imported | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false | Total Apparent Energy Imported
fixed |  | 40156 | 40155 | 65 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40158 | 40157 | 67 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40160 | 40159 | 69 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C | Reserviert | 0 |  | acc32 | VAh | TotVAh_SF | r | nein | false
fixed |  | 40162 | 40161 | 71 | 1 | TotVAh_SF |  | Reserviert | 0 |  | sunssf |  |  | r | nein | false | Apparent Energy scale factor
fixed |  | 40163 | 40162 | 72 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false | Total Reactive Energy Imported Quadrant 1
fixed |  | 40165 | 40164 | 74 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40167 | 40166 | 76 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40169 | 40168 | 78 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40171 | 40170 | 80 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false | Total Reactive Power Imported Quadrant 2
fixed |  | 40173 | 40172 | 82 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40175 | 40174 | 84 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40177 | 40176 | 86 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40179 | 40178 | 88 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false | Total Reactive Power Exported Quadrant 3
fixed |  | 40181 | 40180 | 90 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40183 | 40182 | 92 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40185 | 40184 | 94 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40187 | 40186 | 96 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false | Total Reactive Power Exported Quadrant 4
fixed |  | 40189 | 40188 | 98 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40191 | 40190 | 100 | 2 | TotVArhExpQ4PhB |  | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40193 | 40192 | 102 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | Reserviert | 0 |  | acc32 | varh | TotVArh_SF | r | nein | false
fixed |  | 40195 | 40194 | 104 | 1 | TotVArh_SF |  | Reserviert | 0 |  | sunssf |  |  | r | nein | false | Reactive Energy scale factor
fixed |  | 40196 | 40195 | 105 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | true | Meter Event Flags | Siehe Kapitel 16.4. Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist.
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM01 |  |  | 16
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM02 |  |  | 17
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM03 |  |  | 18
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM04 |  |  | 19
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM01 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM02 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM01 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM04 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: Signing Meter
Model: BSM Meter
Description: Meter data which goes beyond the scope of an AC meter.
Notes:
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40198 | 40197 | 0 | 1 | ID | Model ID | Modell-ID | 64900 | 64900 | uint16 |  |  | r | nein | true |  | Eigener Block Signierender Zähler
header |  | 40199 | 40198 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 292 | 292 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40200 | 40199 | 2 | 4 | ErrM | Error Code Meter | Fehler-Code Zählermodul |  |  | string |  |  | r | nein | false | Meter module error code | Dieser Fehlercode wird in einem Bit des Feldes ‚Evt‘ des Modells des Dreiphasenzählers | This error code gets summarized in 'Evt' from the AC meter model 203.
fixed |  | 40204 | 40203 | 6 | 8 | SNM | Serial Number Meter | Seriennummer Zählermodul |  |  | string |  |  | r | nein | false | Serial number meter module |  | This serial number is also provided as 'SN' in common model (1).
fixed |  | 40212 | 40211 | 14 | 8 | SNC | Serial Number Communication Module | Seriennummer Kommunikationsmodul |  |  | string |  |  | r | nein | false | Serial number of the meter's communication module
fixed |  | 40220 | 40219 | 22 | 8 | VrM | Software Version Meter | Software-Version Zählermodul |  |  | string |  |  | r | nein | false | Meter firmware version and checksum | Hierin wird auch die Prüfsumme dieser Firmware angegeben | This version informatin is also provided as 'Vr' in common model (1).
fixed |  | 40228 | 40227 | 30 | 8 | VrC | Software Version Communication Module | Software-Version Kommunikationsmodul |  |  | string |  |  | r | nein | false | Communication module firmware version | Die Prüfsumme dieser Firmware ist in der Instanz ‚Communication Module Firmware Hash‘ des BLOB-Modells (64902) zu finden. | The firmware hash is provided separately via the 'Communication Module Firmware Hash' instance of the 'BLOB' model (64902).
fixed |  | 40236 | 40235 | 38 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false | Meter address 1
fixed |  | 40244 | 40243 | 46 | 8 | MA2 | Meter Address 2 | Adresse 2 |  |  | string |  |  | r | nein | false | Meter address 2
fixed |  | 40252 | 40251 | 54 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | uint32 | Wh | RCR_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This data point value gets reset to zero during the turn-on sequence.
fixed |  | 40254 | 40253 | 56 | 1 | RCR_SF | Real Energy Imported Since Last Turn-On Sequence Scale Factor | Skalierungsfaktor Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | sunssf |  |  | r | nein | false
fixed |  | 40255 | 40254 | 57 | 2 | PDCnt | Power Down Counter | Zähler Spannungsausfall | 0 |  | uint32 |  |  | r | nein | false
fixed |  | 40257 | 40256 | 59 | 2 | RCnt | Response Counter | Paginierungsindex/Antwortzähler | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot | Anzahl der bisher von diesem Gerät signierten Schnappschüsse | This is a counter which gets incremented with and included in each created snapshot. It is used among all snapshot instances.
fixed |  | 40259 | 40258 | 61 | 2 | OS | Operation-Seconds Counter | Sekundenindex/Betriebssekunden | 0 |  | uint32 | s |  | r | nein | false |  | Betriebssekunden dieses Gerätes
fixed |  | 40261 | 40260 | 63 | 2 | Epoch | Current Epoch Time | Aktuelle Uhrzeit | 0 |  | uint32 | s |  | rw | ja | false | Current local time in seconds since 1970 | Epoch-Time, "Unix-Zeit", Sekunden seit dem 1.1.1970 00:00 | Set both, 'Epoch' and 'TZO' in a single write operation for initially setting the time (if the time is invalid, for example after a power-up).
fixed |  | 40263 | 40262 | 65 | 1 | TZO | Timezone Offset | Aktueller Zeitzonen-Offset | 0 |  | int16 | min |  | rw | ja | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. Set both, 'Epoch' and 'TZO' in a single write operation for initially setting the time (if the time is invalid, for example after a power-up).
fixed |  | 40264 | 40263 | 66 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set
fixed |  | 40266 | 40265 | 68 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time
fixed |  | 40268 | 40267 | 70 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs | Niederwertigstes Bit enthält den Zustand des Digitaleingangs
fixed |  | 40269 | 40268 | 71 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | rw | ja | false | Status of the digital outputs | Schreiben des niederwertigsten Bits Register schaltet den Ausgang
fixed |  | 40270 | 40269 | 72 | 2 | DIChgOS | Digital Inputs Last Changed At Operation-Seconds | Sekundenindex letzte Modifikation Digital-Inputs | 0 |  | uint32 | s |  | r | nein | false | The point in time (operation-seconds) when the digital inputs changed last
fixed |  | 40272 | 40271 | 74 | 2 | DIChgEpoch | Digital Inputs Last Changed At Epoch Time | Zeitstempel letzte Modifikation Digital-Inputs | 0 |  | uint32 | s |  | r | nein | false | The point in time (epoch time) when the digital inputs changed last
fixed |  | 40274 | 40273 | 76 | 1 | DIChgTZO | Digital Inputs Last Changed Timezone Offset | Offset UTC letzte Modifikation Digital Inputs | 0 |  | int16 | min |  | r | nein | false | The timezone offset when digital input changed last
fixed |  | 40275 | 40274 | 77 | 2 | DOChgOS | Digital Outputs Last Changed At Operation-Seconds | Sekundenindex letzte Modifikation Digital-Outputs | 0 |  | uint32 | s |  | r | nein | false | The point in time (operation-seconds) when the digital outputs changed last
fixed |  | 40277 | 40276 | 79 | 2 | DOChgEpoch | Digital Outputs Last Changed At Epoch Time | Zeitstempel letzte Modifikation Digital-Outputs | 0 |  | uint32 | s |  | r | nein | false | The point in time (epoch time) when the digital outputs changed last
fixed |  | 40279 | 40278 | 81 | 1 | DOChgTZO | Digital Outputs Last Changed Timezone Offset | Offset UTC letzte Modifikation Digital-Outputs | 0 |  | int16 | min |  | r | nein | false | The timezone offset when digital outputs changed last
fixed |  | 40280 | 40279 | 82 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | rw | ja | false | User metadata 1 | Metadaten, die in Schnappschüsse aufgenommen werden, Identifkationsdaten für OCMF | Use this data point for including custom data into signed snapshots.
fixed |  | 40350 | 40349 | 152 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | rw | ja | false | User metadata 2 | Metadaten, die in Schnappschüsse aufgenommen werden | Use this data point for including custom data into signed snapshots.
fixed |  | 40400 | 40399 | 202 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | rw | ja | false | User metadata 3 | Metadaten, die in Schnappschüsse aufgenommen werden | Use this data point for including custom data into signed snapshots.
fixed |  | 40450 | 40449 | 252 | 1 | NPK | Number Of Public-Key Registers | BLOB-Register in PK | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the public key BLOB area | Anzahl der wiederholenden Blöcke PK des BLOB-Bereichs des öffentlichen Schlüssels
fixed |  | 40451 | 40450 | 253 | 1 | BPK | Number Of Public-Key Bytes | BLOB-Bytes in PK | 0 |  | uint16 |  |  | r | nein | false | The length of the public key BLOB provided by PK in bytes | Tatsächliche Anzahl Bytes des öffentlichen Schlüssels
repeating |  | 40452 | 40451 | 0 | 1 | PK | Public Key | Öffentlicher Schlüssel | 0 |  | uint16 |  |  | r | nein | false | The meter's public key used for signing | Wiederholender Block mit Binärdaten des öffentlichen Schüssels im DER-Format | The public key takes up the first BPK bytes from this block, interpreting the individual registers as big endian. The public key is encoded as DER according to RFC 5480.
Model Instance: Communication Module Firmware Hash
Model: BSM BLOB data
Description: A model for exposing binary data (BLOB, binary large object)
Notes: This model is used for exposing BLOB (binary large objects) data which could not be provided by repeating blocks of other models.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40500 | 40499 | 0 | 1 | ID | Model ID | Modell-ID | 64902 | 64902 | uint16 |  |  | r | nein | true |  | Modell Binärdaten
header |  | 40501 | 40500 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 20 | 20 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40502 | 40501 | 2 | 1 | Typ | BLOB Type | BLOB-Typ | 0 |  | enum16 |  |  | r | nein | false | Which BLOB data gets provided by this model instance
fixed |  | 40503 | 40502 | 3 | 1 | NB | Number Of BLOB Registers | BLOB Register B | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the BLOB data area | Anzahl der wiederholenden Blöcke B des Firmware-Hash-BLOBs | This is the space actually reserved in B. The BLOB data's actual length is given in bytes by BB.
fixed |  | 40504 | 40503 | 4 | 1 | BB | Number Of BLOB Bytes | BLOB Bytes in B | 0 |  | uint16 |  |  | r | nein | false | The number of bytes actually representing BLOB data in B | Tatsächliche Anzahl Bytes des Firmware-Hash-BLOBs
fixed |  | 40505 | 40504 | 5 | 1 | Pad | Pad | Padding | 0 |  | pad |  |  | r | nein | false
repeating |  | 40506 | 40505 | 0 | 1 | B | BLOB data | Firmware-Hash | 0 |  | uint16 |  |  | r | nein | false |  | Wiederholender Block mit dem Firmware-Hash (SHA-256). | The BLOB takes up the first BB bytes from this block, interpreting the individual registers as big endian.
enum16 | Typ |  |  |  |  | CM_FIRMWARE_HASH | Communication Module Firmware Hash |  | 0 | [7 empty] | This model instance provides the communication module's firmware hash (SHA-256)
Model Instance: Signed Current Snapshot
Model: BSM Signed Snapshot
Description: A signed snapshot of data from different model instances
Notes: See notes on 'St' for snapshot creation.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40522 | 40521 | 0 | 1 | ID | Model ID | Modell-ID | 64901 | 64901 | uint16 |  |  | r | nein | true |  | Modell Schnappschuss
header |  | 40523 | 40522 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 260 | 260 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40524 | 40523 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 0 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierter Momentanzustand, Siehe Kapitel
fixed |  | 40525 | 40524 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | rw | ja | false | Status of this snapshot instance | Siehe Kapitel | Write 'UPDATING' to this data point for triggering the creation of a new snapshot. Poll this data points afterwards until its value changes to something different from 'UPDATING'.
fixed |  | 40526 | 40525 | 4 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This value ist taken from BSM model 64900. It will be zero in snapshots for the turn-on sequence.
fixed |  | 40528 | 40527 | 6 | 2 | TotWhExp | Total Watt-hours Exported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Total Real Energy Imported |  | This value is taken from AC meter model 203.
fixed |  | 40530 | 40529 | 8 | 1 | Wh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | false | Real energy scale factor
fixed |  | 40531 | 40530 | 9 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | false | Total Real Power |  | This value is taken from AC meter model 203.
fixed |  | 40532 | 40531 | 10 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | false | Real Power scale factor
fixed |  | 40533 | 40532 | 11 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 40541 | 40540 | 19 | 2 | RCnt | Response Counter | Paginierungsindex dieses Snapshots | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot |  | This is a counter which gets incremented with each created snapshot and used among all snapshot instances. You can find the last assigned value in the BSM meter model 64900.
fixed |  | 40543 | 40542 | 21 | 2 | OS | Operation-Seconds Counter | Sekundenindex dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 40545 | 40544 | 23 | 2 | Epoch | Current Epoch Time | Zeitstempel dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false | Current local time in seconds since 1970 |  | This value is taken from BSM meter model 64900.
fixed |  | 40547 | 40546 | 25 | 1 | TZO | Timezone Offset | Offset UTC dieses Snapshots | 0 |  | int16 | min |  | r | nein | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. This value is taken from BSM meter model 64900.
fixed |  | 40548 | 40547 | 26 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set |  | This value is taken from BSM meter model 64900.
fixed |  | 40550 | 40549 | 28 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time |  | This value is taken from BSM meter model 64900.
fixed |  | 40552 | 40551 | 30 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs |  | This value is taken from BSM meter model 64900.
fixed |  | 40553 | 40552 | 31 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital outputs |  | This value is taken from BSM meter model 64900.
fixed |  | 40554 | 40553 | 32 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | r | nein | false | User metadata 1 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40624 | 40623 | 102 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | r | nein | false | User metadata 2 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40674 | 40673 | 152 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | r | nein | false | User metadata 3 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40724 | 40723 | 202 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | false | Meter Event Flags | Siehe Kapitel 16.4., Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist. | This value is taken from AC meter model 203.
fixed |  | 40726 | 40725 | 204 | 1 | NSig | Number Of Signature Registers | Länge Signaturblock | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the signature BLOB area | Anzahl der wiederholenden Blöcke Sig der Signatur | This is the space acutally reserved in Sig. The signature data's actual length is given in bytes by BSig.
fixed |  | 40727 | 40726 | 205 | 1 | BSig | Number Of Signature Bytes | Länge der Signatur in Bytes | 0 |  | uint16 |  |  | r | nein | false | Number of bytes actually representing signature data in Sig. | Tatsächliche Anzahl Bytes der Signatur
repeating |  | 40728 | 40727 | 0 | 1 | Sig | Digital Signature | Signatur | 0 |  | uint16 |  |  | r | nein | false | The snapshot's ECDSA signature | Wiederholender Block mit Binärdaten der Signatur im DER-Format | The signature takes up the first BSig bytes from this block, interpreting the individual registers as big endian. It is encoded as DER according to RFC 4492.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_Meter_Fatal_Error | Meter Fatal Error |  | 16 | [7 empty] | The meter module reported a fatal error |  | This bit summarizes the meter module's error status 'Err' from BSM model (64900). It gets set when this value differs from 0000000. This is a fatal error. Values returned by the device are no longer guaranteed to be valid.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Init_Failed | Communication Module Startup Initialization Failed |  | 17 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Firmware_Hash_Mismatch | Communication Module Firmware Hash Mismatch |  | 18 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Development_Mode | Communication Module in Development Mode |  | 19 | [9 empty] | This is a device in development mode. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: Signed Turn-On Snapshot
Model: BSM Signed Snapshot
Description: A signed snapshot of data from different model instances
Notes: See notes on 'St' for snapshot creation.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 40776 | 40775 | 0 | 1 | ID | Model ID | Modell-ID | 64901 | 64901 | uint16 |  |  | r | nein | true |  | Modell Schnappschuss
header |  | 40777 | 40776 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 260 | 260 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 40778 | 40777 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 1 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Schalt-Mess-Koordination Einschalten, Siehe Kapitel 16.4.
fixed |  | 40779 | 40778 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | rw | ja | false | Status of this snapshot instance | Siehe Kapitel 16.4., Schreiben von aktualisieren löst das Erstellen aus | Write 'UPDATING' to this data point for triggering the creation of a new snapshot. Poll this data points afterwards until its value changes to something different from 'UPDATING'.
fixed |  | 40780 | 40779 | 4 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This value ist taken from BSM model 64900. It will be zero in snapshots for the turn-on sequence.
fixed |  | 40782 | 40781 | 6 | 2 | TotWhExp | Total Watt-hours Exported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Total Real Energy Imported |  | This value is taken from AC meter model 203.
fixed |  | 40784 | 40783 | 8 | 1 | Wh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | false | Real energy scale factor
fixed |  | 40785 | 40784 | 9 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | false | Total Real Power |  | This value is taken from AC meter model 203.
fixed |  | 40786 | 40785 | 10 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | false | Real Power scale factor
fixed |  | 40787 | 40786 | 11 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 40795 | 40794 | 19 | 2 | RCnt | Response Counter | Paginierungsindex dieses Snapshots | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot |  | This is a counter which gets incremented with each created snapshot and used among all snapshot instances. You can find the last assigned value in the BSM meter model 64900.
fixed |  | 40797 | 40796 | 21 | 2 | OS | Operation-Seconds Counter | Sekundenindex dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 40799 | 40798 | 23 | 2 | Epoch | Current Epoch Time | Zeitstempel dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false | Current local time in seconds since 1970 |  | This value is taken from BSM meter model 64900.
fixed |  | 40801 | 40800 | 25 | 1 | TZO | Timezone Offset | Offset UTC dieses Snapshots | 0 |  | int16 | min |  | r | nein | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. This value is taken from BSM meter model 64900.
fixed |  | 40802 | 40801 | 26 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set |  | This value is taken from BSM meter model 64900.
fixed |  | 40804 | 40803 | 28 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time |  | This value is taken from BSM meter model 64900.
fixed |  | 40806 | 40805 | 30 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs |  | This value is taken from BSM meter model 64900.
fixed |  | 40807 | 40806 | 31 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital outputs |  | This value is taken from BSM meter model 64900.
fixed |  | 40808 | 40807 | 32 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | r | nein | false | User metadata 1 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40878 | 40877 | 102 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | r | nein | false | User metadata 2 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40928 | 40927 | 152 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | r | nein | false | User metadata 3 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 40978 | 40977 | 202 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | false | Meter Event Flags | Siehe Kapitel 16.4., Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist. | This value is taken from AC meter model 203.
fixed |  | 40980 | 40979 | 204 | 1 | NSig | Number Of Signature Registers | Länge Signaturblock | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the signature BLOB area | Anzahl der wiederholenden Blöcke Sig der Signatur | This is the space acutally reserved in Sig. The signature data's actual length is given in bytes by BSig.
fixed |  | 40981 | 40980 | 205 | 1 | BSig | Number Of Signature Bytes | Länge der Signatur in Bytes | 0 |  | uint16 |  |  | r | nein | false | Number of bytes actually representing signature data in Sig. | Tatsächliche Anzahl Bytes der Signatur
repeating |  | 40982 | 40981 | 0 | 1 | Sig | Digital Signature | Signatur | 0 |  | uint16 |  |  | r | nein | false | The snapshot's ECDSA signature | Wiederholender Block mit Binärdaten der Signatur im DER-Format | The signature takes up the first BSig bytes from this block, interpreting the individual registers as big endian. It is encoded as DER according to RFC 4492.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_Meter_Fatal_Error | Meter Fatal Error |  | 16 | [7 empty] | The meter module reported a fatal error |  | This bit summarizes the meter module's error status 'Err' from BSM model (64900). It gets set when this value differs from 0000000. This is a fatal error. Values returned by the device are no longer guaranteed to be valid.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Init_Failed | Communication Module Startup Initialization Failed |  | 17 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Firmware_Hash_Mismatch | Communication Module Firmware Hash Mismatch |  | 18 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Development_Mode | Communication Module in Development Mode |  | 19 | [9 empty] | This is a device in development mode. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: Signed Turn-Off Snapshot
Model: BSM Signed Snapshot
Description: A signed snapshot of data from different model instances
Notes: See notes on 'St' for snapshot creation.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 41030 | 41029 | 0 | 1 | ID | Model ID | Modell-ID | 64901 | 64901 | uint16 |  |  | r | nein | true |  | Modell Schnappschuss
header |  | 41031 | 41030 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 260 | 260 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 41032 | 41031 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 2 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Schalt-Mess-Koordination Ausschalten, Siehe Kapitel 16.4.
fixed |  | 41033 | 41032 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | rw | ja | false | Status of this snapshot instance | Siehe Kapitel 16.4., Schreiben von aktualisieren löst das Erstellen aus | Write 'UPDATING' to this data point for triggering the creation of a new snapshot. Poll this data points afterwards until its value changes to something different from 'UPDATING'.
fixed |  | 41034 | 41033 | 4 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This value ist taken from BSM model 64900. It will be zero in snapshots for the turn-on sequence.
fixed |  | 41036 | 41035 | 6 | 2 | TotWhExp | Total Watt-hours Exported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Total Real Energy Imported |  | This value is taken from AC meter model 203.
fixed |  | 41038 | 41037 | 8 | 1 | Wh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | false | Real energy scale factor
fixed |  | 41039 | 41038 | 9 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | false | Total Real Power |  | This value is taken from AC meter model 203.
fixed |  | 41040 | 41039 | 10 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | false | Real Power scale factor
fixed |  | 41041 | 41040 | 11 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41049 | 41048 | 19 | 2 | RCnt | Response Counter | Paginierungsindex dieses Snapshots | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot |  | This is a counter which gets incremented with each created snapshot and used among all snapshot instances. You can find the last assigned value in the BSM meter model 64900.
fixed |  | 41051 | 41050 | 21 | 2 | OS | Operation-Seconds Counter | Sekundenindex dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41053 | 41052 | 23 | 2 | Epoch | Current Epoch Time | Zeitstempel dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false | Current local time in seconds since 1970 |  | This value is taken from BSM meter model 64900.
fixed |  | 41055 | 41054 | 25 | 1 | TZO | Timezone Offset | Offset UTC dieses Snapshots | 0 |  | int16 | min |  | r | nein | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. This value is taken from BSM meter model 64900.
fixed |  | 41056 | 41055 | 26 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set |  | This value is taken from BSM meter model 64900.
fixed |  | 41058 | 41057 | 28 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time |  | This value is taken from BSM meter model 64900.
fixed |  | 41060 | 41059 | 30 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41061 | 41060 | 31 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital outputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41062 | 41061 | 32 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | r | nein | false | User metadata 1 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41132 | 41131 | 102 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | r | nein | false | User metadata 2 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41182 | 41181 | 152 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | r | nein | false | User metadata 3 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41232 | 41231 | 202 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | false | Meter Event Flags | Siehe Kapitel 16.4., Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist. | This value is taken from AC meter model 203.
fixed |  | 41234 | 41233 | 204 | 1 | NSig | Number Of Signature Registers | Länge Signaturblock | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the signature BLOB area | Anzahl der wiederholenden Blöcke Sig der Signatur | This is the space acutally reserved in Sig. The signature data's actual length is given in bytes by BSig.
fixed |  | 41235 | 41234 | 205 | 1 | BSig | Number Of Signature Bytes | Länge der Signatur in Bytes | 0 |  | uint16 |  |  | r | nein | false | Number of bytes actually representing signature data in Sig. | Tatsächliche Anzahl Bytes der Signatur
repeating |  | 41236 | 41235 | 0 | 1 | Sig | Digital Signature | Signatur | 0 |  | uint16 |  |  | r | nein | false | The snapshot's ECDSA signature | Wiederholender Block mit Binärdaten der Signatur im DER-Format | The signature takes up the first BSig bytes from this block, interpreting the individual registers as big endian. It is encoded as DER according to RFC 4492.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_Meter_Fatal_Error | Meter Fatal Error |  | 16 | [7 empty] | The meter module reported a fatal error |  | This bit summarizes the meter module's error status 'Err' from BSM model (64900). It gets set when this value differs from 0000000. This is a fatal error. Values returned by the device are no longer guaranteed to be valid.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Init_Failed | Communication Module Startup Initialization Failed |  | 17 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Firmware_Hash_Mismatch | Communication Module Firmware Hash Mismatch |  | 18 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Development_Mode | Communication Module in Development Mode |  | 19 | [9 empty] | This is a device in development mode. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: Signed Start Snapshot
Model: BSM Signed Snapshot
Description: A signed snapshot of data from different model instances
Notes: See notes on 'St' for snapshot creation.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 41284 | 41283 | 0 | 1 | ID | Model ID | Modell-ID | 64901 | 64901 | uint16 |  |  | r | nein | true |  | Modell Schnappschuss
header |  | 41285 | 41284 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 260 | 260 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 41286 | 41285 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 3 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Messung Start, Siehe Kapitel 16.4.
fixed |  | 41287 | 41286 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | rw | ja | false | Status of this snapshot instance | Siehe Kapitel 16.4., Schreiben von aktualisieren löst das Erstellen aus | Write 'UPDATING' to this data point for triggering the creation of a new snapshot. Poll this data points afterwards until its value changes to something different from 'UPDATING'.
fixed |  | 41288 | 41287 | 4 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This value ist taken from BSM model 64900. It will be zero in snapshots for the turn-on sequence.
fixed |  | 41290 | 41289 | 6 | 2 | TotWhExp | Total Watt-hours Exported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Total Real Energy Imported |  | This value is taken from AC meter model 203.
fixed |  | 41292 | 41291 | 8 | 1 | Wh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | false | Real energy scale factor
fixed |  | 41293 | 41292 | 9 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | false | Total Real Power |  | This value is taken from AC meter model 203.
fixed |  | 41294 | 41293 | 10 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | false | Real Power scale factor
fixed |  | 41295 | 41294 | 11 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41303 | 41302 | 19 | 2 | RCnt | Response Counter | Paginierungsindex dieses Snapshots | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot |  | This is a counter which gets incremented with each created snapshot and used among all snapshot instances. You can find the last assigned value in the BSM meter model 64900.
fixed |  | 41305 | 41304 | 21 | 2 | OS | Operation-Seconds Counter | Sekundenindex dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41307 | 41306 | 23 | 2 | Epoch | Current Epoch Time | Zeitstempel dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false | Current local time in seconds since 1970 |  | This value is taken from BSM meter model 64900.
fixed |  | 41309 | 41308 | 25 | 1 | TZO | Timezone Offset | Offset UTC dieses Snapshots | 0 |  | int16 | min |  | r | nein | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. This value is taken from BSM meter model 64900.
fixed |  | 41310 | 41309 | 26 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set |  | This value is taken from BSM meter model 64900.
fixed |  | 41312 | 41311 | 28 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time |  | This value is taken from BSM meter model 64900.
fixed |  | 41314 | 41313 | 30 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41315 | 41314 | 31 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital outputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41316 | 41315 | 32 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | r | nein | false | User metadata 1 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41386 | 41385 | 102 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | r | nein | false | User metadata 2 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41436 | 41435 | 152 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | r | nein | false | User metadata 3 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41486 | 41485 | 202 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | false | Meter Event Flags | Siehe Kapitel 16.4., Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist. | This value is taken from AC meter model 203.
fixed |  | 41488 | 41487 | 204 | 1 | NSig | Number Of Signature Registers | Länge Signaturblock | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the signature BLOB area | Anzahl der wiederholenden Blöcke Sig der Signatur | This is the space acutally reserved in Sig. The signature data's actual length is given in bytes by BSig.
fixed |  | 41489 | 41488 | 205 | 1 | BSig | Number Of Signature Bytes | Länge der Signatur in Bytes | 0 |  | uint16 |  |  | r | nein | false | Number of bytes actually representing signature data in Sig. | Tatsächliche Anzahl Bytes der Signatur
repeating |  | 41490 | 41489 | 0 | 1 | Sig | Digital Signature | Signatur | 0 |  | uint16 |  |  | r | nein | false | The snapshot's ECDSA signature | Wiederholender Block mit Binärdaten der Signatur im DER-Format | The signature takes up the first BSig bytes from this block, interpreting the individual registers as big endian. It is encoded as DER according to RFC 4492.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_Meter_Fatal_Error | Meter Fatal Error |  | 16 | [7 empty] | The meter module reported a fatal error |  | This bit summarizes the meter module's error status 'Err' from BSM model (64900). It gets set when this value differs from 0000000. This is a fatal error. Values returned by the device are no longer guaranteed to be valid.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Init_Failed | Communication Module Startup Initialization Failed |  | 17 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Firmware_Hash_Mismatch | Communication Module Firmware Hash Mismatch |  | 18 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Development_Mode | Communication Module in Development Mode |  | 19 | [9 empty] | This is a device in development mode. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: Signed End Snapshot
Model: BSM Signed Snapshot
Description: A signed snapshot of data from different model instances
Notes: See notes on 'St' for snapshot creation.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 41538 | 41537 | 0 | 1 | ID | Model ID | Modell-ID | 64901 | 64901 | uint16 |  |  | r | nein | true |  | Modell Schnappschuss
header |  | 41539 | 41538 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 260 | 260 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 41540 | 41539 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 4 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Messung Ende, Siehe Kapitel 16.4.
fixed |  | 41541 | 41540 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | rw | ja | false | Status of this snapshot instance | Siehe Kapitel 16.4., Schreiben von aktualisieren löst das Erstellen aus | Write 'UPDATING' to this data point for triggering the creation of a new snapshot. Poll this data points afterwards until its value changes to something different from 'UPDATING'.
fixed |  | 41542 | 41541 | 4 | 2 | RCR | Real Energy Imported Since Last Turn-On Sequence | Energiebezug seit der letzten Schalt-Mess-Koordination Einschalten | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Real energy imported since the last execution of the turn-on sequence |  | This value ist taken from BSM model 64900. It will be zero in snapshots for the turn-on sequence.
fixed |  | 41544 | 41543 | 6 | 2 | TotWhExp | Total Watt-hours Exported | Wirkenergiezähler Bezug | 0 |  | acc32 | Wh | Wh_SF | r | nein | false | Total Real Energy Imported |  | This value is taken from AC meter model 203.
fixed |  | 41546 | 41545 | 8 | 1 | Wh_SF |  | Skalierungsfaktor Wirkenergie | 0 |  | sunssf |  |  | r | nein | false | Real energy scale factor
fixed |  | 41547 | 41546 | 9 | 1 | W | Watts | Momentane Wirk-Leistung Total | 0 |  | int16 | W | W_SF | r | nein | false | Total Real Power |  | This value is taken from AC meter model 203.
fixed |  | 41548 | 41547 | 10 | 1 | W_SF |  | Skalierungsfaktor Wirkleistung | 0 |  | sunssf |  |  | r | nein | false | Real Power scale factor
fixed |  | 41549 | 41548 | 11 | 8 | MA1 | Meter Address 1 | Adresse 1 |  |  | string |  |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41557 | 41556 | 19 | 2 | RCnt | Response Counter | Paginierungsindex dieses Snapshots | 0 |  | uint32 |  |  | r | nein | false | A counter incremented with each snapshot |  | This is a counter which gets incremented with each created snapshot and used among all snapshot instances. You can find the last assigned value in the BSM meter model 64900.
fixed |  | 41559 | 41558 | 21 | 2 | OS | Operation-Seconds Counter | Sekundenindex dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false |  |  | This value is taken from BSM meter model 64900.
fixed |  | 41561 | 41560 | 23 | 2 | Epoch | Current Epoch Time | Zeitstempel dieses Snapshots | 0 |  | uint32 | s |  | r | nein | false | Current local time in seconds since 1970 |  | This value is taken from BSM meter model 64900.
fixed |  | 41563 | 41562 | 25 | 1 | TZO | Timezone Offset | Offset UTC dieses Snapshots | 0 |  | int16 | min |  | r | nein | false | Timezone offset of local epoch time time to UTC |  | Positive values refer to time zones east/ahead of UTC, negative values to time zones west/behind of UTC. This value is taken from BSM meter model 64900.
fixed |  | 41564 | 41563 | 26 | 2 | EpochSetCnt | Time Set Counter | Zähler Stellen Aktuelle Uhrzeit UTC | 0 |  | uint32 |  |  | r | nein | false | How many time epoch time and timezone offset have been set |  | This value is taken from BSM meter model 64900.
fixed |  | 41566 | 41565 | 28 | 2 | EpochSetOS | Time Last Set At Operation-Seconds | Letztes Stellen der Aktuellen Uhrzeit UTC (Betriebssekunden) | 0 |  | uint32 | s |  | r | nein | false | Operation-seconds when the time has been set the last time |  | This value is taken from BSM meter model 64900.
fixed |  | 41568 | 41567 | 30 | 1 | DI | Digital Input State | Zustand Digital-Inputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital inputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41569 | 41568 | 31 | 1 | DO | Digital Output State | Zustand Digital-Outputs | 0 |  | uint16 |  |  | r | nein | false | Status of the digital outputs |  | This value is taken from BSM meter model 64900.
fixed |  | 41570 | 41569 | 32 | 70 | Meta1 | Metadata 1 | Metadaten 1 |  |  | string |  |  | r | nein | false | User metadata 1 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41640 | 41639 | 102 | 50 | Meta2 | Metadata 2 | Metadaten 2 |  |  | string |  |  | r | nein | false | User metadata 2 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41690 | 41689 | 152 | 50 | Meta3 | Metadata 3 | Metadaten 3 |  |  | string |  |  | r | nein | false | User metadata 3 | Metadaten, die beim Anfertigen und signieren eines Schnappschusses mit einbezogen werden | This value is taken from BSM meter model 64900.
fixed |  | 41740 | 41739 | 202 | 2 | Evt | Events | Ereignisse | 0 |  | bitfield32 |  |  | r | nein | false | Meter Event Flags | Siehe Kapitel 16.4., Ereignis-Flags kritischer Ereignisse von Zähler- und Kommunikationsmodul. Ein Problem liegt vor, wenn dieser Wert verschieden von Null ist. | This value is taken from AC meter model 203.
fixed |  | 41742 | 41741 | 204 | 1 | NSig | Number Of Signature Registers | Länge Signaturblock | 0 |  | uint16 |  |  | r | nein | false | The number of registers of the signature BLOB area | Anzahl der wiederholenden Blöcke Sig der Signatur | This is the space acutally reserved in Sig. The signature data's actual length is given in bytes by BSig.
fixed |  | 41743 | 41742 | 205 | 1 | BSig | Number Of Signature Bytes | Länge der Signatur in Bytes | 0 |  | uint16 |  |  | r | nein | false | Number of bytes actually representing signature data in Sig. | Tatsächliche Anzahl Bytes der Signatur
repeating |  | 41744 | 41743 | 0 | 1 | Sig | Digital Signature | Signatur | 0 |  | uint16 |  |  | r | nein | false | The snapshot's ECDSA signature | Wiederholender Block mit Binärdaten der Signatur im DER-Format | The signature takes up the first BSig bytes from this block, interpreting the individual registers as big endian. It is encoded as DER according to RFC 4492.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
bitfield32 | Evt |  |  |  |  | M_EVENT_Power_Failure |  |  | 2
bitfield32 | Evt |  |  |  |  | M_EVENT_Under_Voltage |  |  | 3
bitfield32 | Evt |  |  |  |  | M_EVENT_Low_PF |  |  | 4
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Current |  |  | 5
bitfield32 | Evt |  |  |  |  | M_EVENT_Over_Voltage |  |  | 6
bitfield32 | Evt |  |  |  |  | M_EVENT_Missing_Sensor |  |  | 7
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved1 |  |  | 8
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved2 |  |  | 9
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved3 |  |  | 10
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved4 |  |  | 11
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved5 |  |  | 12
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved6 |  |  | 13
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved7 |  |  | 14
bitfield32 | Evt |  |  |  |  | M_EVENT_Reserved8 |  |  | 15
bitfield32 | Evt |  |  |  |  | M_EVENT_Meter_Fatal_Error | Meter Fatal Error |  | 16 | [7 empty] | The meter module reported a fatal error |  | This bit summarizes the meter module's error status 'Err' from BSM model (64900). It gets set when this value differs from 0000000. This is a fatal error. Values returned by the device are no longer guaranteed to be valid.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Init_Failed | Communication Module Startup Initialization Failed |  | 17 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Firmware_Hash_Mismatch | Communication Module Firmware Hash Mismatch |  | 18 | [9 empty] | This is a fatal error. Values returned by the device are no longer guaranteed to be valid. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_CM_Development_Mode | Communication Module in Development Mode |  | 19 | [9 empty] | This is a device in development mode. Do not consider signed data as authentic.
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM05 |  |  | 20
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM06 |  |  | 21
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM07 |  |  | 22
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM08 |  |  | 23
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM09 |  |  | 24
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM10 |  |  | 25
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM11 |  |  | 26
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM12 |  |  | 27
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM13 |  |  | 28
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM14 |  |  | 29
bitfield32 | Evt |  |  |  |  | M_EVENT_OEM15 |  |  | 30
bitfield32 | Evt | [5 empty] | Power Failure | [9 empty] | Loss of power or phase
bitfield32 | Evt | [5 empty] | Under Voltage | [9 empty] | Voltage below threshold (Phase Loss)
bitfield32 | Evt | [5 empty] | Low PF | [9 empty] | Power Factor below threshold
bitfield32 | Evt | [5 empty] | Over Current | [9 empty] | Current Input over threshold
bitfield32 | Evt | [5 empty] | Over Voltage | [9 empty] | Voltage Input over threshold
bitfield32 | Evt | [5 empty] | Missing Sensor | [9 empty] | Sensor not connected
bitfield32 | Evt | [5 empty] | OEM05 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM06 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM07 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM08 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM09 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM10 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM11 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM12 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM13 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM14 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM15 | [9 empty] | Reserved for OEM use
bitfield32 | Evt | [5 empty] | OEM16 | [9 empty] | Reserved for OEM use
Model Instance: OCMF Signed Current Snapshot
Model: BSM Signed OCMF Data
Description: An OCMF representation of a BSM Signed Snapshot (model ID 64901). Signed snapshots and their OCMF representations are matched by the 'Typ' data point. The OCMF representation contains selected data from the underlying snapshot. For example, 'Meta1' is taken as identity information and the other metadata data points are omitted.
Notes: Use the underlying snapshot's 'St' data point for creating snapshot data. Once the snapshot is valid, you could read its OCMF representation from here.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 41792 | 41791 | 0 | 1 | ID | Model ID | Modell-ID | 64903 | 64903 | uint16 |  |  | r | nein | true |  | Modell OCMF-Daten
header |  | 41793 | 41792 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 372 | 372 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 41794 | 41793 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 0 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierter Momentanzustand, Siehe Kapitel
fixed |  | 41795 | 41794 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | r | nein | false | Status of this snapshot instance | Siehe Kapitel | Write to the underlying snapshot's data point 'St' to trigger an update. 'St' is read-only here.
fixed |  | 41796 | 41795 | 4 | 496 | O | OCMF | OCMF-Darstellung des Schnappschusses |  |  | string |  |  | r | nein | false | OCMF representation of the snapshot indicated by 'Typ' | OCMF-Darstellung des Schnappschusses signierter Momentanzustand, das Metadatenfeld 1 wird als OCMF-Identität benutzt | See https://github.com/SAFE-eV/OCMF-Open-Charge-Metering-Format/blob/e1c25620533400405340cfddc0dc71574939f1c5/OCMF-de.md for more information about OCMF.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to the underlying snapshot's data point 'St' to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
Model Instance: OCMF Signed Turn-On Snapshot
Model: BSM Signed OCMF Data
Description: An OCMF representation of a BSM Signed Snapshot (model ID 64901). Signed snapshots and their OCMF representations are matched by the 'Typ' data point. The OCMF representation contains selected data from the underlying snapshot. For example, 'Meta1' is taken as identity information and the other metadata data points are omitted.
Notes: Use the underlying snapshot's 'St' data point for creating snapshot data. Once the snapshot is valid, you could read its OCMF representation from here.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 42292 | 42291 | 0 | 1 | ID | Model ID | Modell-ID | 64903 | 64903 | uint16 |  |  | r | nein | true |  | Modell OCMF-Daten
header |  | 42293 | 42292 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 372 | 372 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 42294 | 42293 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 1 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Schalt-Mess-Koordination Einschalten, Siehe Kapitel 16.4.
fixed |  | 42295 | 42294 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | r | nein | false | Status of this snapshot instance | Siehe Kapitel | Write to the underlying snapshot's data point 'St' to trigger an update. 'St' is read-only here.
fixed |  | 42296 | 42295 | 4 | 496 | O | OCMF | OCMF-Darstellung des Schnappschusses |  |  | string |  |  | r | nein | false | OCMF representation of the snapshot indicated by 'Typ' | OCMF-Darstellung des Schnappschusses zur signierten Schalt-Mess-Koordination Einschalten, das Metadatenfeld 1 wird als OCMF-Identität benutzt | See https://github.com/SAFE-eV/OCMF-Open-Charge-Metering-Format/blob/e1c25620533400405340cfddc0dc71574939f1c5/OCMF-de.md for more information about OCMF.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to the underlying snapshot's data point 'St' to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
Model Instance: OCMF Signed Turn-Off Snapshot
Model: BSM Signed OCMF Data
Description: An OCMF representation of a BSM Signed Snapshot (model ID 64901). Signed snapshots and their OCMF representations are matched by the 'Typ' data point. The OCMF representation contains selected data from the underlying snapshot. For example, 'Meta1' is taken as identity information and the other metadata data points are omitted.
Notes: Use the underlying snapshot's 'St' data point for creating snapshot data. Once the snapshot is valid, you could read its OCMF representation from here.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 42792 | 42791 | 0 | 1 | ID | Model ID | Modell-ID | 64903 | 64903 | uint16 |  |  | r | nein | true |  | Modell OCMF-Daten
header |  | 42793 | 42792 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 372 | 372 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 42794 | 42793 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 2 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Schalt-Mess-Koordination Ausschalten, Siehe Kapitel 16.4.
fixed |  | 42795 | 42794 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | r | nein | false | Status of this snapshot instance | Siehe Kapitel | Write to the underlying snapshot's data point 'St' to trigger an update. 'St' is read-only here.
fixed |  | 42796 | 42795 | 4 | 496 | O | OCMF | OCMF-Darstellung des Schnappschusses |  |  | string |  |  | r | nein | false | OCMF representation of the snapshot indicated by 'Typ' | OCMF-Darstellung des Schnappschusses zur signierten Schalt-Mess-Koordination Ausschalten, das Metadatenfeld 1 wird als OCMF-Identität benutzt | See https://github.com/SAFE-eV/OCMF-Open-Charge-Metering-Format/blob/e1c25620533400405340cfddc0dc71574939f1c5/OCMF-de.md for more information about OCMF.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to the underlying snapshot's data point 'St' to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
Model Instance: OCMF Signed Start Snapshot
Model: BSM Signed OCMF Data
Description: An OCMF representation of a BSM Signed Snapshot (model ID 64901). Signed snapshots and their OCMF representations are matched by the 'Typ' data point. The OCMF representation contains selected data from the underlying snapshot. For example, 'Meta1' is taken as identity information and the other metadata data points are omitted.
Notes: Use the underlying snapshot's 'St' data point for creating snapshot data. Once the snapshot is valid, you could read its OCMF representation from here.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 43292 | 43291 | 0 | 1 | ID | Model ID | Modell-ID | 64903 | 64903 | uint16 |  |  | r | nein | true |  | Modell OCMF-Daten
header |  | 43293 | 43292 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 372 | 372 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 43294 | 43293 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 3 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Messung Start, Siehe Kapitel 16.4.
fixed |  | 43295 | 43294 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | r | nein | false | Status of this snapshot instance | Siehe Kapitel | Write to the underlying snapshot's data point 'St' to trigger an update. 'St' is read-only here.
fixed |  | 43296 | 43295 | 4 | 496 | O | OCMF | OCMF-Darstellung des Schnappschusses |  |  | string |  |  | r | nein | false | OCMF representation of the snapshot indicated by 'Typ' | OCMF-Darstellung des Schnappschusses zur signierten Schalt-Mess-Koordination Ausschalten, das Metadatenfeld 1 wird als OCMF-Identität benutzt | See https://github.com/SAFE-eV/OCMF-Open-Charge-Metering-Format/blob/e1c25620533400405340cfddc0dc71574939f1c5/OCMF-de.md for more information about OCMF.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to the underlying snapshot's data point 'St' to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).
Model Instance: OCMF Signed End Snapshot
Model: BSM Signed OCMF Data
Description: An OCMF representation of a BSM Signed Snapshot (model ID 64901). Signed snapshots and their OCMF representations are matched by the 'Typ' data point. The OCMF representation contains selected data from the underlying snapshot. For example, 'Meta1' is taken as identity information and the other metadata data points are omitted.
Notes: Use the underlying snapshot's 'St' data point for creating snapshot data. Once the snapshot is valid, you could read its OCMF representation from here.
Field Type | Applicable Point | Data Model Address | Address | Address Offset | Size | Name | Label | Label User Documentation | Value | Default Value User Documentation | Type | Units | Scale Factor | Access SunSpec | Actual Access User Documentation | Mandatory | Description | Description User Documentation | Notes
header |  | 43792 | 43791 | 0 | 1 | ID | Model ID | Modell-ID | 64903 | 64903 | uint16 |  |  | r | nein | true |  | Modell OCMF-Daten
header |  | 43793 | 43792 | 1 | 1 | L | Model Payload Length | Länge Nutzdaten | 372 | 372 | uint16 |  |  | r | nein | true |  | Ohne die Felder ‚Modell-ID‘ und ‚Länge Nutzdaten‘
fixed |  | 43794 | 43793 | 2 | 1 | Typ | Snapshot Type | Typ dieses Snapshots | 0 | 4 | enum16 |  |  | r | nein | false | Which snapshot type is represented by this model instance | Signierte Messung Ende, Siehe Kapitel 16.4.
fixed |  | 43795 | 43794 | 3 | 1 | St | Snapshot Status | Status des Snapshots/Auslöser | 0 |  | enum16 |  |  | r | nein | false | Status of this snapshot instance | Siehe Kapitel | Write to the underlying snapshot's data point 'St' to trigger an update. 'St' is read-only here.
fixed |  | 43796 | 43795 | 4 | 496 | O | OCMF | OCMF-Darstellung des Schnappschusses |  |  | string |  |  | r | nein | false | OCMF representation of the snapshot indicated by 'Typ' | OCMF-Darstellung des Schnappschusses zur signierten Schalt-Mess-Koordination Ausschalten, das Metadatenfeld 1 wird als OCMF-Identität benutzt | See https://github.com/SAFE-eV/OCMF-Open-Charge-Metering-Format/blob/e1c25620533400405340cfddc0dc71574939f1c5/OCMF-de.md for more information about OCMF.
enum16 | Typ |  |  |  |  | CURRENT | Signed Current Snapshot |  | 0 | [7 empty] | Signed snapshot of the current meter data at the time of its creation |  | Creating this snapshot just collects and signs the data. No further action is taken.
enum16 | Typ |  |  |  |  | TURN_ON | Signed Turn-On Snapshot |  | 1 | [7 empty] | Signed snapshot created during executing the turn-on sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken with the contactor turned off.
enum16 | Typ |  |  |  |  | TURN_OFF | Signed Turn-Off Snapshot |  | 2 | [7 empty] | Signed snapshot created during the execution of the turn-off sequence for an external contactor |  | Creating this snapshot executes the turn-on sequence for an external contactor. Its data is taken after turning the contactor off.
enum16 | Typ |  |  |  |  | START | Signed Start Snapshot |  | 3 | [7 empty] | Signed snapshot marking the start of a charging process without executing the turn-on sequence for an external contactor.
enum16 | Typ |  |  |  |  | END | Signed End Snapshot |  | 4 | [7 empty] | Signed snapshot marking the end of a charging process without executing the turn-off sequence for an external contactor
enum16 | St |  |  |  |  | VALID | Snapshot Data Valid |  | 0 | [7 empty] | The model instance contains valid signed data of a snapshot
enum16 | St |  |  |  |  | INVALID | Snapshot Data Invalid |  | 1 | [7 empty] | Snapshot data is invalid. This is the case after powering on the meter.
enum16 | St |  |  |  |  | UPDATING | Snapshot Data Gets Updated |  | 2 | [7 empty] | The snapshot gets currently updated. Snapshot data is invalid. |  | Write this value to the underlying snapshot's data point 'St' to trigger the creation of a new snapshot. Afterwards poll this data point until its value changes to a different symbol indicating the outcome of the update process.
enum16 | St |  |  |  |  | FAILED_GENERAL | Snapshot Creation Failed For Unspecified Reason |  | 3 | [7 empty] | Creating the snapshot failed for an unspecified reason (for example an internal error)
enum16 | St |  |  |  |  | FAILED_NOT_ENABLED | Snapshot Creation Failed Due To Missing Enable Signal |  | 4 | [7 empty] | Creating the snapshot failed due to a missing enable signal (DOE) |  | This could happen when attempting to create a turn-on snapshot.
enum16 | St |  |  |  |  | FAILED_FEEDBACK | Snapshot Creation Failed Due Missing/Wrong Contactor Feedback |  | 5 | [7 empty] | Creating the snapshot failed due to missing or wrong feedback from the external contactor (through DI).